## Tur_StatusCodes
COL | SCADA VARIABLE | BIT | DESCRIPTION
321 | SubPcsPrivStatusWordA | 0 | Converter is ready. All start conditions are fulfilled
321 | SubPcsPrivStatusWordA | 1 | Cooling system is ready.
321 | SubPcsPrivStatusWordA | 2 | It is allowed to float the blades in the wind.
321 | SubPcsPrivStatusWordA | 3 | DC-Link is charged (DC-Link voltage is higher than 90% of UN)
321 | SubPcsPrivStatusWordA | 4 | Protection detects an alarm (at least 1 alarm is pending)
321 | SubPcsPrivStatusWordA | 5 | Protection detects an E-Stop 3 (at least 1 fault is pending)
321 | SubPcsPrivStatusWordA | 6 | Protection detects an E-Stop 1 or 2 (at least 1 fault is pending)
321 | SubPcsPrivStatusWordA | 7 | Protection blocks a restart, system needs maintenance
321 | SubPcsPrivStatusWordA | 9 | Grid Pulses are released (Grid Converter)
321 | SubPcsPrivStatusWordA | 10 | Generator Pulses are released (Generator Converter)
321 | SubPcsPrivStatusWordA | 11 | Grid PLL is locked (GRI is synchronized with the Grid)
321 | SubPcsPrivStatusWordA | 12 | Generator PLL is locked (GEC is synchronized with the Grid)
368 | SubPcsPrivStatusWordB | 0 | Converter is in state: OFF / On Inhibit
368 | SubPcsPrivStatusWordB | 1 | Converter is in state: Standby
368 | SubPcsPrivStatusWordB | 2 | Converter is in state: VAR Compensation
368 | SubPcsPrivStatusWordB | 3 | Converter is in state: Production
368 | SubPcsPrivStatusWordB | 4 | Converter is in state: I/F-Mode
368 | SubPcsPrivStatusWordB | 5 | Converter is in state: U/F-Mode
368 | SubPcsPrivStatusWordB | 6 | Converter is in state: E-Stop 1,2,3
368 | SubPcsPrivStatusWordB | 7 | Converter is in transition between: OFF ↔ Standby
368 | SubPcsPrivStatusWordB | 8 | Converter is in transition between: OFF ↔ I/F-Mode
368 | SubPcsPrivStatusWordB | 9 | Converter is in transition between: OFF ↔ U/F-Mode
368 | SubPcsPrivStatusWordB | 10 | Converter is in transition between: Standby ↔ Production
368 | SubPcsPrivStatusWordB | 11 | Converter is in transition between: Standby ↔ VAR Compensation
368 | SubPcsPrivStatusWordB | 12 | Converter is in transition between: Production ↔ VAR Compensation
368 | SubPcsPrivStatusWordB | 13 | Converter is in an abort sequence (goes back to previous state)
368 | SubPcsPrivStatusWordB | 14 | Converter is in transition to E-Stop 1,2,3
368 | SubPcsPrivStatusWordB | 15 | Converter has faced a sequence timeout between 2 states
367 | SubPcsPrivStatusWordC | 0 | GRB1 is open (Grid Breaker)
367 | SubPcsPrivStatusWordC | 1 | GRB1 is closed (Grid Breaker)
367 | SubPcsPrivStatusWordC | 2 | GEB1 is open (Generator Breaker)
367 | SubPcsPrivStatusWordC | 3 | GEB1 is closed (Generator Breaker)
367 | SubPcsPrivStatusWordC | 4 | GRB2 is open (Grid Breaker)
367 | SubPcsPrivStatusWordC | 5 | GRB2 is closed (Grid Breaker)
367 | SubPcsPrivStatusWordC | 6 | GEB2 is open (Generator Breaker)
367 | SubPcsPrivStatusWordC | 7 | GEB2 is closed (Generator Breaker)
367 | SubPcsPrivStatusWordC | 8 | GRB1 Disconnector is closed (Grid Breaker)
367 | SubPcsPrivStatusWordC | 9 | GEB1 Disconnector is closed (Generator Breaker)
367 | SubPcsPrivStatusWordC | 10 | GRB2 Disconnector is closed (Grid Breaker)
367 | SubPcsPrivStatusWordC | 11 | GEB2 Disconnector is closed (Generator Breaker)
367 | SubPcsPrivStatusWordC | 12 | GRB1 Disconnector is earthed (Grid Breaker)
367 | SubPcsPrivStatusWordC | 13 | GEB1 Disconnector is earthed (Generator Breaker)
367 | SubPcsPrivStatusWordC | 14 | GRB2 Disconnector is earthed (Grid Breaker)
367 | SubPcsPrivStatusWordC | 15 | GEB2 Disconnector is earthed (Generator Breaker)
366 | SubPcsPrivStatusWordD | 4 | Hall test bit is on
366 | SubPcsPrivStatusWordD | 14 | Converter has saved parameters
365 | SubPcsPrivAlmWordA | 0 | VLM temp pos half high
365 | SubPcsPrivAlmWordA | 1 | VLM temp neg half high
365 | SubPcsPrivAlmWordA | 8 | CCU MCB uncrit prot
365 | SubPcsPrivAlmWordA | 9 | CCA MCB uncrit prot
365 | SubPcsPrivAlmWordA | 10 | FCA MCB uncrit prot
365 | SubPcsPrivAlmWordA | 11 | CCU UPS battery mode
365 | SubPcsPrivAlmWordA | 12 | CCA UPS battery mode
365 | SubPcsPrivAlmWordA | 13 | FCA UPS battery mode
364 | SubPcsPrivAlmWordB | 0 | WCU pump 1 alarm
364 | SubPcsPrivAlmWordB | 1 | WCU pump 2 alarm
364 | SubPcsPrivAlmWordB | 2 | CCU temperature high
364 | SubPcsPrivAlmWordB | 3 | CCA temperature high
364 | SubPcsPrivAlmWordB | 4 | FCA temperature high
364 | SubPcsPrivAlmWordB | 5 | WCU water temp high
364 | SubPcsPrivAlmWordB | 6 | WCU CCA water flow low
364 | SubPcsPrivAlmWordB | 7 | WCU FCA water flow low
364 | SubPcsPrivAlmWordB | 8 | WCU conductivity high
364 | SubPcsPrivAlmWordB | 9 | WCU CCA press In low
364 | SubPcsPrivAlmWordB | 10 | WCU CCA press Out low
364 | SubPcsPrivAlmWordB | 11 | WCU FCA press In low
364 | SubPcsPrivAlmWordB | 12 | WCU FCA press Out low
360 | SubPcsPrivFaultWordReturnPtr | 0 | Pointer not valid
360 | SubPcsPrivFaultWordReturnPtr | 1 | WCU Faults
360 | SubPcsPrivFaultWordReturnPtr | 2 | GEC Faults A
360 | SubPcsPrivFaultWordReturnPtr | 3 | GEC Faults B
360 | SubPcsPrivFaultWordReturnPtr | 4 | GRI Faults A
360 | SubPcsPrivFaultWordReturnPtr | 5 | GRI Faults B
360 | SubPcsPrivFaultWordReturnPtr | 6 | DC-Link Faults
360 | SubPcsPrivFaultWordReturnPtr | 7 | System Faults A
360 | SubPcsPrivFaultWordReturnPtr | 8 | System Faults B
360 | SubPcsPrivFaultWordReturnPtr | 9 | Control Faults A
360 | SubPcsPrivFaultWordReturnPtr | 10 | Control Faults B
360 | SubPcsPrivFaultWordReturnPtr | 11 | Control Faults C
360 | SubPcsPrivFaultWordReturnPtr | 12 | Control Faults D
360 | SubPcsPrivFaultWordReturnPtr | 13 | Control Faults E
360 | SubPcsPrivFaultWordReturnPtr | 15 | WCU First Fault
360 | SubPcsPrivFaultWordReturnPtr | 16 | GEC First Fault A
360 | SubPcsPrivFaultWordReturnPtr | 17 | GEC First Fault B
360 | SubPcsPrivFaultWordReturnPtr | 18 | GRI First Fault A
360 | SubPcsPrivFaultWordReturnPtr | 19 | GRI First Fault B
360 | SubPcsPrivFaultWordReturnPtr | 20 | DC-Link First Fault
360 | SubPcsPrivFaultWordReturnPtr | 21 | System First Fault A
360 | SubPcsPrivFaultWordReturnPtr | 22 | System First Fault B
360 | SubPcsPrivFaultWordReturnPtr | 23 | Control First Fault A
360 | SubPcsPrivFaultWordReturnPtr | 24 | Control First Fault B
360 | SubPcsPrivFaultWordReturnPtr | 25 | Control First Fault C
360 | SubPcsPrivFaultWordReturnPtr | 26 | Control First Fault D
360 | SubPcsPrivFaultWordReturnPtr | 27 | Control First Fault E
363 | SubPcsPrivCoolingStateWord | 0 | Pump 1 is running
363 | SubPcsPrivCoolingStateWord | 1 | Pump 2 is running

## Tur_Abbreviations
ABBREVIATION | DESCRIPTION
AC | Alternating Current
ADC | Analog Digital Converter
AI | Analog Input
AO | Analog Output
ASE | Anti Saturation Equipment
CB | Circuit Breaker
CCB | Compact Control Builder
COMBI | Control System for Converters
CPU | Central Processing Unit
CT | Current Transducer
DC | Direct Current
DI | Digital Input
DO | Digital Output
EOFF | Emergency OFF
FPGA | Field Programmable Gate Array
GEB | Generator Breaker
GEC | Generator Converter
GRB | Grid Breaker
GRI | Grid Converter
GU | Gate Unit
HVD | High Voltage Divider
HW | Hardware
IF-Mode | Turbine Positioning Mode
IGCT | Integrated Gate Commutated Thyristor
I/O | Input / Output
IPS | Isolated Power Supply
ML | Multilink
NC | Normally Closed
NO | Normally Open
PC | Personal Computer
PCB | Printed Circuit Board
PCS | Power Converter System
PE | Protective Earth (Protective Ground)
PEC | Power Electronic Converter
PECINTM | Power Electronic Converter Interface & Measurement Board
PLL | Phase Lock Loop
PS | Power Supply
S800 | Input / Output Module
UF-Mode | Turbine Rotation Mode
SW | Software
UPS | Uninterruptible Power Supply
VLSCD | Voltage Limiting Short Circuit Detection
VPN | Virtual Private Network
VT | Voltage Transducer
WT | Wind Turbine